# Distech Controls BACnet Explorer 3.0.0.exe
User Guide

Professional User Manual for the PowerShell/WPF BACnet Explorer

# 1. Introduction

Distech Controls BACnet Explorer 3.0.0 is a lightweight desktop utility designed for commissioning, troubleshooting, and validating BACnet networks. The application allows users to discover BACnet/IP and routed MS/TP devices, browse objects, read and write present values with priority control, manage Out-of-Service states, and export results for documentation and escalation purposes.

# 2. System Requirements and Prerequisites

Before using the application, ensure the following requirements are met:

Windows 10 or Windows 11 (64-bit)

PowerShell 5.1 or later

.NET Framework with WPF assemblies (PresentationFramework, PresentationCore, WindowsBase)

Administrative privileges may be required for UDP socket access

Network requirements:

IPv4-enabled network interface connected to the BACnet segment

UDP port access (default BACnet/IP port 47808)

Firewall rules allowing inbound and outbound BACnet/IP traffic

BACnet/IP routers available for routed MS/TP discovery (if applicable)

# 3. Launching the Application

Distech Controls BACnet Explorer 3.0.0.exe is launched by double-clicking the executable. Upon startup, the application initializes its BACnet client stack, enumerates available network adapters, and opens a diagnostic transcript for logging and export.

# 4. User Interface Overview

The user interface is organized into logical sections to support efficient field operation and clear workflow progression.

## 4.1 Network Configuration Panel

Network Interface: Selects the active IPv4 adapter used for BACnet communication

Local Device ID: Defines the BACnet device instance used by the explorer

UDP Ports: One or more BACnet/IP ports used during discovery

Discovery Timeout: Total time allocated for multi-phase discovery

APDU Timeout and Retries: Controls response handling and reliability

Max APDU Length, Segmentation, and Max Segments: BACnet protocol tuning options

## 4.2 Device Discovery and Device List

The device list displays all discovered BACnet devices, including both native BACnet/IP devices and routed MS/TP devices.

Discover Devices: Initiates a three-phase BACnet discovery process

Refresh Devices: Re-runs discovery using current settings

Add Device: Manually inserts a device by IP address and instance

Clear Devices: Removes all devices from the list

Right-click Remove Device: Deletes a selected device entry

## 4.3 Object Browser and Command Panel

After selecting a device, the object browser allows users to retrieve and interact with BACnet objects hosted by that device.

Read All Properties: Retrieves the device object list and key properties

Object Type Filter: Limits the display to selected BACnet object types

Objects Grid: Displays object type, instance, name, present value, and units

Right-click actions: Refresh object, read priority array, copy name or value

## 4.4 Commanding and Control

Command Value: Numeric input for analog objects or dropdown for binary and multistate

Priority Selection: Allows writing at BACnet priorities 1 through 16

Write: Writes Present Value at the selected priority

Release: Releases the selected priority

Release All: Releases priorities 1 through 15

## 4.5 Out-of-Service and Relinquish Default

Out-of-Service Toggle: Enables commanding of input objects

Relinquish Default Read/Write: Manages the fallback value at priority 16

## 4.6 Export and Logging

Export Objects to CSV: Saves the current object list

Export Devices to CSV: Saves the discovered device list

Export Log: Saves the application transcript for diagnostics

# 5. Common Workflows

This section outlines typical operational tasks performed using the application.

## 5.1 Discovering Devices

Select the appropriate network interface, verify BACnet settings, and click Discover Devices. The application performs broadcast and routed discovery, populating the device list with reachable BACnet devices.

## 5.2 Reading Objects

Select a device and click Read All Properties to retrieve its object list. The application reads object name, present value, units, and state text where applicable.

## 5.3 Writing and Releasing Values

Select an object, enter or select a value, choose a BACnet priority, and click Write. Use Release or Release All to relinquish control and return the object to normal operation.

## 5.4 Managing Input Overrides

For input objects, enable Out-of-Service before writing a value. Always disable Out-of-Service after testing to restore live input behavior.

# 6. Troubleshooting

No devices discovered: Verify network interface, VLAN, and firewall settings

Timeouts or slow reads: Increase APDU timeout or retries

Write access denied: Confirm object type, priority, and device permissions

Out-of-Service write failures: Verify device support for property 111

# 7. Best Practices

Use priority 8 (Manual Operator) for temporary overrides

Release all overrides after commissioning

Export logs and CSVs for documentation and escalation

Avoid leaving inputs in Out-of-Service state